Annex No. 2

TECHNICAL SPECIFICATIONS

for procurement of

“Delivery of Machinery for Waste Water Decantation and Waste Water Recycling“

Basic Characterisation

Subject of the contract is machinery for waste water decantation and waste water recyling, produced as a result of washing process of raw sand and gravel material. The machinery is to be incorporated into the technological circuit of the “screening system” for decantation and water recycling by separating clay particles from the polluted water. Thereafter, the recycled water may be repeatedly used to wash the raw material. The system of the given machinery should be able to operate on full automation and without an operator, whereby the technician shall only be responsible for any needed adjustments and function control of the system.

The machinery shall be stationed outdoors at the premises of the Contracting Authority, sand and gravel quarry Velká Černoc and sand and gravel quarry Straškov. The Contracting Authority requires the supply of two identical machineries. The delivery includes all electrical installations, supporting structural and load bearing elements, pipe systems between the individual devices and any auxiliary materials neccessary for the device to fully operate as intended. The delivery does not include construction work which shall be seperately conducted by the Contracting Authority.

Machinery Description

The technological circuit (hereafter the „screening system“) is composed from the listed components: industrial hopper, discharge conveyor belts, vibrating screener and wheel sand washer. The subject of the delivery (hereafter “assembly“) shall be placed behind the wheel sand washer and connected back to the vibrating screen. The assembly consists of a waste water decantation tank for treatment of the pulleted water, which upon decantation freely overflows into the clear water tank. The sludge that settles down in the waste water tank during the process is then drained from the tank out, into the sludge bed. Clear water is accumulated in a seperate water tank which is then pumped out by a seperate pump back into the screening system.

The table below states the required technical parameters of each specific unit. The parameters are defined either as minimal, maximal, a range or a specific value or attribute.

The bidder shall fill out the empty collumn:

- In case of a quantified parameter: a specific number value which corresponds to the given minimum, maximum or specified value.

- In case of a non-quantifiable parameter: YES/NO dependent on whether the offered unit meets or does not meet the requirement.

In the event that a bidder's offer does not meet the required parameters (i.e. in case of a quantifiable parameter, the offer does not meet the required value and in case of a non-quantifiable parameter, the request will indicate NO), such offer shall be disqualified from the tender.

| MINIMAL TECHNICAL PARAMETERS – (a single assembly) |  |  |  |
| --- | --- | --- | --- |
| In the event of any specified trade names present within the Tender Conditions (hereafter “TC”) or its annexes, such tradenames only define the required standard, whereby the Contracting Authority accepts any technically and qualitatively comparable solutions. The Contracting Authority does not permit variant solutions or bids beyond the requirements of the TC. Any unmet criterias shall amount to failure of meeting the required parameters and serves as grounds for disqualification. |  |  |  |
| Parameter | Requirement | Unit | Enter the appropriate numeric value or YES/NO answers |
| 1) Waste water decantation tank (steel) |  |  |  |
| number of units | 1 | unit |  |
| treatment capacity | between 700 – 750 | m3/h |  |
| diameter | between 13 500 - 14 000 | mm |  |
| height | between 3000 - 3500 | mm |  |
| steel thickness | min. 4 | mm |  |
| galvanised finish | YES | - |  |
| Required components: |  |  |  |
| fixed bridge installed on the water decnatation, equipped with a gearbox unit to lift up the scraper | YES | - |  |
| stairway to enter the bridge | YES | - |  |
| fixed bridge equipped with a walking platform and railings | YES | - |  |
| galvanised finished of the bridge | YES | - |  |
| dosage tank for injecting the flocculant substance installed on top of the water decantation tank | YES | - |  |
| central pipeline for gravity fed supply of the contaminated water into the waste water decantation tank | YES | - |  |
| 2) Motorised scraper (sludge scraping unit ) |  |  |  |
| scarping paddles for slurry collection into the collecting cone | YES | - |  |
| motor gearbox connected to the driving wheel of the scraper | YES | - |  |
| automatic system for scraper lifting | YES | - |  |
| control system for current absorption of the motor driving the rotation of the scrapers | YES | - |  |
| 3) Equipment for slurry drainage from the bottom of the waste water decantation tank |  |  |  |
| centrifugal sludge pump | YES |  |  |
| hourly capacity | between min. 120 | m3/h |  |
| 4) Flocculant station |  |  |  |
| number of connected tanks | min.2, max. 3 | unit |  |
| corrosion resistant steel container for flocculant powder | YES | - |  |
| motor pump for batch delivery of the flocculant programmable according to specific requirements | YES | - |  |

| 5) Flocculant Analyser |  |  |  |
| --- | --- | --- | --- |
| control system for flocculant concetration in the water through decanting water sampling | YES | - |  |
| automatic adjustment of working parameters for the flocculant dosing pump in accordance to the settling speed of the suspended solids within the sample | YES | - |  |
| 6) Electric Panel Board |  |  |  |
| touch screen panel | YES | - |  |
| possibility of individual replacement in case of malfunction | YES | - |  |
| capsule protection against adverse weather conditions/exposure to the outdoors | YES | - |  |
| 7) Clear water tank (concrete bottom floor) |  |  |  |
| number of units | 1 | unit |  |
| steel thickness | min. 4 | mm |  |
| diameter | between 9 500 – 10 000 | mm |  |
| height | between 2800 – 3000 | mm |  |
| capacity | min. 220 | m3 |  |
| 8) Pumps for recycled clear water |  |  |  |
| number of units | 2 | unit |  |
| flow rate | between 300 - 350 | m3/h |  |
| delivery height | between 25 – 50 | m |  |
| power | between 37 – 45 | kW |  |
| 9) Other Accessories |  |  |  |
| Pipelines connecting seperate units | YES | - |  |

The bidder hereby declares that declared bid for the machinery delivery fullfills the above stated parameters and requirements.

In	Date

…………………………………………………………………………………………

Signiture of the authorised person acting on behalf of the bidder